## Slide 1: Comparison of Heat Exchanger Types Shannon Murphy, Conor Sandin, Erin Tiedemann Department of Chemical Engineering, University of New Hampshire
Results
Methods
Introduction
References
Discussion
Each heat exchanger was operated using Armfield software, which regulated:
Inlet temperature of hot fluid (35˚C)
Flow rates of both fluids
Flow patterns (cocurrent vs countercurrent)
Thermocouples monitored temperature changes at every inlet and outlet
Each trial was collected in triplicate for both flow patterns
[1] MIT, Concentric tube heat exchangers. 2012.
[2] Indian Institute of Technology Delh, Two Shell Pass- Four Tube Pass Heat Exchanger. 2016.
[3] Indian Institute of Technology Delhi, Gasketed Plate and Frame Heat Exchanger. 1988
[4]Heat Exchanger Theory, 1st ed. 2016
[5]C. Geankoplis, Transport processes and unit operations. Engelwood Cliffs, N.J.: PTR Prentice Hall, 1993.
Countercurrent flow increased the overall heat transfer coefficient of a system for all exchanger types
The plate heat exchanger tested had the largest U, which is due to the large surface area of heat transfer available
The tubular heat exchanger and shell heat exchanger had similar heat transfer coefficients due to their lower surface area to volume ratios
Design Problem
Design problem: Identify the heat exchanger design required to heat a 3kg/s liquid reactant stream from 20°C to 50°C with available hot water at 80°C.
Heat exchangers are used to transfer heat between one or more fluids.
The heat is transferred along the following path:
convection through the hot fluid
conduction through the wall
convection through the cold fluid
The rate of heat transfer is determined by calculating the overall heat transfer coefficient and the log mean temperature difference of a system.
(1)
(2)
The overall heat transfer coefficient and rate of heat transfer for a system are used to maximize the operation efficiency of heat exchangers
The three type of heat exchangers in this study are tubular [1], shell-and-tube [2], and plate [3] heat exchangers.
This study investigated the effects of flow pattern and flow rate on the overall heat transfer coefficient for the three types of heat exchangers.
Based on the data collected in this study, conditions producing the highest U are:
Plate heat exchanger
Countercurrent conditions
For all types tested, increasing flow rates increased the overall heat transfer coefficient of the system.
Statistical analysis showed that flow type did not significantly effect U, and yielded regression models for each exchanger type.
Figure 3. Effect of hot and cold flow rates on the overall heat transfer coefficient, U. Flow types are represented by dark (countercurrent) and light (co-current) shades. Blue represents varying hot flow rates at a constant cold flow rate, and red represents the opposite.
Table 2. Regression model coefficients. |  | 
Heat Exchanger Type | Cold | Hot
Plate | 1366.3 | 1568.0
Tube | 568.9 | 233.5
Shell | 286.6 | 303.8
Table 3. Design Problem Data |  | 
NRe | Diameter (m) | As (m2)
983.18 | 0.54 | 7.20
(3)
A plate heat exchanger with countercurrent conditions and an area of heat transfer of 7.2m2 is recommended.
Table 1. Average U values for various heat exchangers |  | 
Heat Exchanger Type | U (W/m2K) | 
 | Co-Current | Countercurrent
Plate | 1638.8 | 4029.3
Tubular | 419.2 | 949.7
Shell and Tube | 494.7 | 840.9
 | Hot Flow Rate |  | 
Cold Flow Rate | 1 | 2 | 3
 | 2 |  | 
 | 3 |  | 
Figure 2. Flow types and data collection. Countercurrent (A) and co-current (B) flow types. On the right is a matrix describing data collection: one inlet flow is varied while the other is held constant.
A
B
The Reynolds number for the experimental cold flow rate was calculated, and was scaled up to determine the design specifications.
U (W/m2K)
Flow Rate (L/min)
Chart: 
| 1.0 | 2.0 | 3.0
 | 1804.3909 | 4051.5422 | 7116.958
 | 1804.3909 | 3663.2488 | 6453.7505
 | 1195.9861 | 2163.3722 | 4388.6506
 | 1195.9861 | 2622.467 | 4176.089
 | 491.8124 | 1005.477 | 1707.6077
 | 491.8124 | 1277.3131 | 2137.6959
 | 408.1359 | 768.2563 | 1224.3613
 | 408.1359 | 1223.3112 | 2107.8678
 | 301.1465 | 866.9447 | 1372.7744
 | 301.1465 | 766.8968 | 1325.4057
 | 529.926 | 816.31 | 1207.654
 | 529.926 | 739.4333 | 1257.6032
Plate Heat Exchanger
Tubular Heat Exchanger
Shell-and-Tube Heat Exchanger